Author: mngo
Last saved by: ali
Company: Hewlett-Packard Company

DIVISION 27 21 29
Vi2400WP MaxiiCopper™ High Speed IP67 Weatherproof Ethernet Mini Extenders over Coax Cables
PART 1 - GENERAL
1.01	SUMMARY
A.	Weatherproof IP67 Ethernet Extender over Coax cables 

1.02	SECTION INCLUDES
A.	Vi2400WP Single Port Ethernet Extender Over Coax Using Symmetric Bandwidth (SBW^TM) and Pass Through PoE (PTP^TM) Technology 

1.03	REFERENCES
A.	CE - European Union Compliance (CE)
B.	RoHS - Restriction of Use of Hazardous Substances
C.	WEEE - Waste Electrical and Electronic Equipment Directive
D.	UL - Underwriters Laboratory
E.	RFC - Request for Comments
F.	IEEE - Institute of Electrical and Electronics Engineers
G.	EN/IEC - International Electrotechnical Commission

1.04	SYSTEM DESCRIPTION
A.	Performance Requirements: Provide 1 Ethernet extended distance 10/100BaseT port and 1 10/100Base-TX standard port.
B.	The system shall utilize TIA/EIA 568-B cable connected to an RJ45 plug for standard Ethernet.
C.	The system shall utilize a BNC 1978 standard IEC 169-8 connector for extended transmission.

1.05	SUBMITTALS
A.	Manufacturer’s Installation and Operating Manual: Printed installation and operating information
B.	Warranty: Manufacturer’s Printed Warranty

1.06	DELIVERY, STORAGE AND HANDLING
A.	Store in original packaging in a climate controlled environment. 
B.	Storage Temperature not to exceed: -40˚C to +85˚C

1.07	PROJECT/SITE CONDITIONS
A.	Temperature Requirements: Product shall operate in an environment with an ambient temperature range of -40˚C to +75˚C without the assistance of fan-forced cooling.
B.	Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 90% (non-condensing). 

1.08	WARRANTY
A.	Limited Life Time Warranty: Vigitron guarantees product to be free of defects for product lifetime, defined as the time that product is in production plus 3 years from end of production.

PART 2 – PRODUCTS

2.1	MANUFACTURER
A.	Acceptable Manufacturer: 
1.	Vigitron, Inc. 7810 Trade Street, Suite 100, San Diego, CA 92121, USA 
2.	Phone 1-858-484-5209
3.	Email: support@vigitron.com
B.	Substitutions: Not Permitted

2.2	MANUFACTURED UNITS
A.	Reference Table A: Product Number, Descriptions and Maximum Distance
B.	Reference Table B: IEEE Product Compatibility Chart
C.	Reference Table C: Product System Compatibility Chart

2.3	GENERAL SPECIFICATIONS
A.	The 1-port Coax Ethernet extender shall be Vi2400WP. 
B.	Standard Ethernet Ports:
1.	The device shall have one 10/100BaseT standard Ethernet ports in a compact housing:
a.	The Ethernet port will comply with: 
i.	IEEE 802.3u 10baseT 
ii.	IEEE 802.3u 100baseT 
2.	The Standard Ports will be compliant to IEC 60603-7.
3.	The device shall support Standard Ethernet UTP connection distances up to 100 meters.
4.	The device will be compliant to 802.3af and 802.3at Type 1 and 2 standards.
5.	The Bandwidth selection will be done by automatic detection.
6.	The device shall be used as either transmitter or receiver in the same system.
C.	The Extended Distance Ethernet Ports:
1.	Will support distances up to 5,000 feet (1,524m) at 10BaseT. 
2.	Will support distances up to 1,800 feet (548m) at 100BaseT. 
3.	Will support the ability to pass 802.3af/at PoE from a source to a device at the stated distances. 
4.	Will support 10/100BaseT and PoE at following distances:
a.	802.3af at 1,500 ft. (457m)
b.	802.3at at 500 ft. (152m)
7.	Will maintain all 802.3af/at safety standards for PSE and PD communications. 
8.	The system will provide the ability to test and verify connection status, and operating bandwidth between two transceivers over the extended connection.
D.	The device will be powered by PoE. 
E.	Unit will consume less than 1.5W of power when external power is used and 1.8W when PoE is provided.
F.	The device shall provide below LED indicators for monitoring proper system operation:
1.	Power - Red indicates power on
2.	Extended distance traffic/Link – Orange
G.	Off - No traffic
H.	Flashing – Traffic
3.	Extended Bandwidth indication:
a.	10BaseT - Green indicating 10BaseT
b.	100BaseT - Orange indicating 100BaseT
4.	Standard Ethernet Connections: Green
a.	Off indicating no connection 
b.	Flashing - connection with traffic

5.	Standard Ethernet Bandwidth indication
a.	10/100BaseT Yellow
b.	Off - no connection 
c.	On - connection is valid
I.	The unit will automatically sense the optimum bandwidth and adjust accordingly.
J.	The Vi2400WP will provide IP67 weatherproof and water proof protection. 
K.	The Vi2400WP will comply to IEC60068-2-52 for operation in salt laden environments. 

2.4	DATA SPECIFICATIONS
A.	Data Interface: Passage of data compliant to: 
1.	RFC 768 UDP
2.	RFC 2068 HTTP
3.	RFC 793 TCP
4.	RFC 791 IP
5.	RFC 1783 TFTP
6.	RFC 894 IP over Ethernet
7.	RFC 2544 TCP/IP Packet Transmission
B.	Data Rate: 10/100 Mbps
C.	Data Connections: 1 standard Ethernet ports and 1 extended Ethernet ports

2.5	Vi2400WP FEATURE SETS
A.	The extender device will transmit and receive data using Symmetric Bandwidth (SBW™). 
1.	Bandwidth will be constant over the quoted extended distance with no more than a 5% decrease, when the input signal varies from a size of 64 bytes to 4500 bytes using bidirectional transmission.
2.	Bandwidth will be constant over the quoted extended distance with no more than 5% decrease when: 
a.	Bidirectional signals are transmitted with a packet size of 4,500 bytes.
b.	Unidirectional signals are transmitted with a packet size of 9,000 bytes.
c.	Bandwidth will remain the same for both upload and download operation.
B.	Packet losses will be at 2% or less at packet sizes, ranging from 64 bytes to 4,500 bytes bidirectional and 9,000 bytes unidirectional.
C.	Packet losses will be at 2% or less at packet sizes of 4500 in bidirectional transmission.
D.	Packets per second (PPS) will not vary more than 5% at packet sizes, ranging from 64 bytes to 4500 bytes.
E.	Packet per second (PPS) will not vary more than 5% at packet of 4500 bytes in bidirectional transmission.
F.	Maximum distance will be 5,000 ft. (1,524m) at 10BaseT. 
G.	Maximum distance will be 1,800 ft. (548m) at 100BaseT. 
H.	Extender device must have the ability to function as a transceiver. 
I.	Extender device must have the ability to be powered using IEEE 802.3at or IEEE 802.3af PoE. 
J.	Extender device must have the ability to operate using Pass Through PoE (PTP™) with a single PoE source, providing power to both transceivers and PD device conforming to 802.3af/at standards. 
K.	Extender device must have the ability to pass through PoE functionality in compliance with IEEE 802.3af/at standards when communicating with a PD: 
1.	Pass through detection pulses from PSE to PD.
2.	Pass through classification pulses from PSE to PD.
3.	Pass through required power from PSE to PD. 
4.	Ability to provide Class 2 802.3af at maximum extended distance to both transceivers and PD from a PoE source. 
5.	Ability to provide Class 0, 1, 2, 3 and 4 802.3af/at power to both transceivers and PD from a PoE source depending on cable length.

L.	Extender must be able to operate in extended temperature environments of -40˚C to +75˚C type tested in compliance to NEMA-TS2 testing procedures.
M.	Extender must provide the ability to test extended distance connection continuity and bandwidth by means of LED indicators. 
N.	Installation can be accomplished without connector removal  

2.6	CONNECTORS
A.	Power: 2-pin TERM BLOCK HDR 3.81MM 2POS
B.	Extended Ethernet Port: BNC 1978 standard, IEC 169-8 with mini coax pigtail 
C.	Ethernet Port: RJ-45 : IEC 60603-7

2.7	ELECTRICAL SPECIFICATIONS
A.	Power Inputs
1.	PoE, 1.8W max 

2.8	MECHANICAL SPECIFICATIONS
A.	Surface Mount Dimensions: 1.81x7.59x1.57 in., 46x193x40 mm  (HxWxL) 
B.	Finish: Extruded Aluminum 
C.	Weight : 0.56lb (254g) 

2.9	ENVIRONMENTAL SPECIFICATIONS
A.	Operating Temp: -40˚C to +75˚C
B.	Storage Temp: -40˚C to +85˚C
C.	Relative Humidity: 0% to 95% (non-condensing)
D.	Enclosure: Compliant to IP67standards 

2.10	REGULATORY AGENCIES/APPROVALS AND LISTINGS
A.	FCC Part 15, Subpart B, Class B 2010
B.	Emission Standards: 
1.	FCC Part 15, Subpart B, Class B 2010
2.	EN 55022:206+A1:2007
3.	EN61000-3-2:2006+A1:2009+A2:2009
4.	EN 61000-3-3:2008
5.	EN55024:1998+A1:2001+A2:2003
C.	Safety:
1.	CSA C22.2 NO. 60950-1-07-CAN/CSA INFORMATION TECHNOLOGY EQUIPMENT SAFETY PART GENERAL REQUIREMENTS - Edition 2 - Revision Date 2011/12/19 (Pending) 
2.	UL 60950-1 INFORMATION TECHNOLOGY EQUIPMENT - SAFETY - PART 1: GENERAL REQUIREMENTS - Edition 2 - Revision Date 2011/12/19 (Pending) 
D.	RoHS
E.	CE

2.11	ACCESSORIES
A.	Operation Manual

2.12	MANUFACTURED UNITS REFERENCE TABLES

PRODUCT | DESCRIPTION | MAX. DISTANCE*

Vi2400WP

Ethernet Extender over Coax

5,000 ft. (1,524m) @ 10BaseT
1,800 ft. (548m) @ 100BaseT

Table A: Product Number Descriptions
*Distance and performance figures are obtained using in-house testing mirroring typical installations. Factors such as cabling, connections, use of power and environmental conditions may affect actual distance, and should be taken in consideration.

PRODUCT | | COMPATIBLE IEEE STANDARDS

Vi2400WP

IEEE 802.3u     IEEE 802.3af      
IEEE 802.3at

Fast Ethernet standard for 10/100TX
Power over Ethernet
Power over Ethernet

Table B: Product IEEE Compatibility Chart 

PRODUCT | COMPATIBLE ETHERNET EQUIPMENT

Vi2400WP

Vi2401A Single port Coax Ethernet Extender
Vi2400A  Single port  mini Coax Ethernet Extender
Vi2404A 4-port Coax Ethernet Extender
Vi2408A 8-port Coax Ethernet Extender
Vi2416A 16-port Coax Ethernet Extender
Vi2601 Single port Extended Coax Midspan
Vi2608 8-port Extended Coax Midspan
Vi2616 16-port Extended Coax Midspan

Table C: Product System Compatibility Chart

Vigitron reserves the right to change products or specifications without notice

END OF SECTION