Title: Vi2401 A&E specifications
Author: Neil Heller
Last saved by: admin6
Company: HP

Vigitron A&E Product Specifications

DIVISION 27 21 29
Vi22301 MaxiiPower™ IEEE 802.3af/at 12/24VDC 60W PoE Splitter
PART 1 - GENERAL
1.01 SUMMARY
A.	PoE splitter providing +12VDC, +24VDC and PoE from 15.4W, 30W and 60W PoE sources 
1.02 SECTION INCLUDES
A.	Vi22301 MaxiiPower^TM 802.3af/at and 60W PoE Splitter 
1.03 REFERENCES
A.	CE - European Union Compliance
B.	RoHS - Restriction of Use of Hazardous Substances
C.	WEEE - Waste Electrical and Electronic Equipment Directive 
D.	UL - Underwriters Laboratory
E.	RFC - Request for Comments 
F.	IEEE - Institute of Electrical and Electronics Engineers
G.	EN/IEC - International Electrotechnical Commission
1.04 SYSTEM DESCRIPTION
A.	Connection Requirements: Provide one extended Ethernet port with BNC connector and one 10/100Base-TX copper port.
1.	The system shall utilize a 1-pair or 4-pair Category 5/5e/6 cable terminated in RJ45 connector with EIA568-B configuration and for extended 10Base-T or 100Base-T.
2.	The system shall utilize a 1-pair or 4-pair Category 5/5e/6 cable terminated in RJ45 connector with EIA568-B configuration and for standard 10Base-T or 100Base-T and PoE. 
3.	The system shall utilize all four pairs when 60W is provided as a PoE source 
4.	The system will be able to provide a DC and PoE output subject to the  
1.05 SUBMITTALS
A.	Manufacturer’s Installation and Operating Manual: Printed Installation and Operating Information
B.	Warranty: Manufacturer’s Printed Warranty
1.06 DELIVERY, STORAGE AND HANDLING
A.	Store in original packaging in a climate controlled environment. 
B.	Storage temperature not to exceed: -40˚C to +85˚C
1.07 PROJECT/SITE CONDITIONS
A.	Temperature Requirements: Product shall operate in an environment with an ambient temperature range of -40˚C to +75˚C without the assistance of fan-forced cooling.
B.	Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 90% (non-condensing). 
1.08 WARRANTY
A.	Limited Lifetime Warranty: Vigitron guarantees product to be free of defects for product’s lifetime, defined as the time that product is in production plus 3 years from the end of production.
PART 2 - PRODUCTS
2.01	 MANUFACTURER
A.	Acceptable Manufacturer: 
1.	Vigitron, Inc. 7810 Trade Street, Suite 100, San Diego, CA 92121, USA 
2.	Phone 1-858-484-5209
3.	Email: support@vigitron.com
B.	Substitutions: Not Permitted
2.02	 MANUFACTURED UNITS
A.	Reference Table A: Product Number Descriptions and Maximum distance 
B.	Reference Table B: IEEE Product Compatibility Chart
C.	Reference Table C: Product System Compatibility Chart 
2.03	 GENERAL SPECIFICATIONS
A.	The Ethernet UTP extender shall be Vi22301.
B.	Ethernet Port:
1.	The module shall support the Ethernet data IEEE 802.3/802.3u 10/100Base-TX protocol.
2.	Bandwidth settings will be by means of a dip switch.
3.	The module features one fixed 10/100TX electrical ports in a compact mini box.
a.	The Ethernet port will comply with: 
i.	IEEE 802.3 10base-T 
ii.	IEEE 802.3u 100base-T 
4.	The extended and standard ports will be compliant to IEC 60603-7.
5.	The module shall support standard Ethernet UTP connection distances up to 328 feet (100m).
C.	With a 15.4W PoE source, the Vi22301 will be able to:
1.	Provide 12.5VDC @ 1 amp over a distance of 328 feet (100m).
2.	When combined with either the Vi2300 series or Vi2400 series extender, the Vi23201 will be able to provide 24VDC @ 0.5 amps over a distance of 2,000 feet (606m). 
3.	Will be able to provide PoE power based on the amount of total power shared with DC output up to 2W at full DC power allocation.

D.	With a 30W PoE source, the Vi22301 will be able to: 
1.	Provide 24VDC @ 1 amp over a distance of 328 feet (100m).
2.	When combined with either the Vi2300 series or Vi2400 series extender, the Vi22301 will be able to provide 24VDC over a distance of 2,000 feet (606m).
3.	Provide 12VDC @ 2 amps over a distance of 328 feet (100m).
4.	Will be able to provide PoE power based on the amount of total power shared with DC output up to 6W at full DC power allocation
E. With a 60W PoE source, the Vi22301 will be able to: 
	1. Provide 12VDC @ 2 amps over distances up to 2,000 feet 
	2. Provide 24VDC @ 1 amp over distances up to 2,000 feet 
3. Will be able to provide PoE power based on the amount of total power shared with DC output up to 36W at full DC power allocation.
F. The unit will have auto speed selection of 10Mbps or 100Mbps operating at either full or half duplex. 
G. The unit will indicate the presence of PoE with a red LED and operation at 12V with a green LED. 
H. The unit will receive power via standard RJ45 connector and output power via a push connector. 
I. The unit will have a slide switch for selecting a 30W or 60W input.
	1. In the 30W setting, 802.3af or 802.3at sources will be used 
2. In the 60W setting PoE sources must provide the ability to power two internal PDs each conforming to 802.3at.	
4.04	DATA SPECIFICATIONS
A.	Data Interface: Passage of Data Compliant to: 
1.	RFC 768 UDP
2.	RFC 2068 HTTP
4.	RFC 793 TCP
5.	RFC 791 IP	
6.	RFC 1783 TFTP
7.	RFC 894 IP over Ethernet
8.	RFC 2544 TCP/IP Packet Transmission
B.	Data Rate: 10/100Mbps
C.	Data + PoE: 2
1.	Two RJ45 IEC 60603-7
4.05	SPECIFICATIONS AND FEATURE SETS
A.	The unit will receive data plus PoE.
1.	The unit will split data and PoE, allowing DC and Data+ PoE output.
2.	The output voltage will be selected by means of a slide switch.
B.	The power source shall conform to IEEE standards for 802.3af, 802.3at PoE and 60W sources.
C.	The extender must have the ability to pass through PoE in compliance to IEEE 802.3af/at standards when communicating with a PD.
1.	Pass through detection pulses from PSE to PD.
2.	Pass through class pulses from PSE to PD.
3.	Pass through required power from PSE to PD.
4.	Ability to cease power transmission in the event of short or other abnormal conditions.
D.	The extender must be able to operate in extended temperature environments of: -40˚C to +75˚C type tested in compliance to NEMA-TS2 testing procedures.
E.	The extender must provide the ability to test extended distance connection continuity and bandwidth by means of LED display. 

4.06	CONNECTORS

4.07	ELECTRICAL SPECIFICATIONS
A.	Power Inputs 
1.	IEEE 802.3af PoE 15.4W @ 48VDC 
2.	IEEE 802.3at PoE 30W @ 57VDC 
3.	60W @ 57VDC 
3.08	MECHANICAL SPECIFICATIONS
A.	Dimensions: 1.36 X 2.13 x 2.91 in.; 34.5 x 54.1 x 73.9 cm (HxWxL) 
B.	Finish: Module shall be constructed of a metal enclosure. 
C.	Weight: 0.25 lbs (115g)
2.09	 ENVIRONMENTAL SPECIFICATIONS
A.	Operating Temp: -40˚C to +85˚C
B.	Storage Temp: -65˚C to +150˚C
C.	Relative Humidity: 0% to 90% (non-condensing)
2.10	REGULATORY AGENCIES/APPROVALS AND LISTINGS
A.	FCC Part 15, Subpart B, Class B 2010
B.	RoHS
C.	CE
2.11	ACCESSORIES
A.	Operational Manual
2.12	MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions 
Model Number | Description | Max. Distance*
Vi22301 | IEEE 802.3af/at 12/24VDC 60WPoE Splitter | 328 Feet (100m)
* Distance and performance figures are obtained using in house testing mirroring installation. Factors such as cabling, connections, use of power, and environmental conditions may affect actual distance and should be taken in consideration.

Table B: Product IEEE Compatibility Chart
Extended Ethernet Transceiver | Compatible IEEE Standards

Vi22301

IEEE 802.3u Fast Ethernet Standard for 10/100TX Protocol
IEEE 802.3af Power over Ethernet 
IEEE 802.3at Power over Ethernet
60W PoE compatible with dual PD 802.3at x 2

Vigitron reserves the right to change products or specifications without notice.
END OF SECTION

Vigitron Vi22301 A&E Specification | Page  of | March 2017