Author: mngo
Last saved by: ali
Company: Hewlett-Packard Company

DIVISION 27 21 29
Vi3002 Ethernet and 60W PoE Repeater
PART 1 - GENERAL
1.01	SUMMARY
A.	Ethernet and 60W PoE repeater over UTP cables 
	
1.02	SECTION INCLUDES
A.	Vi3002 UTP IP and 60W PoE Repeater

1.03	REFERENCES
A.	CE - European Union Compliance (CE)
B.	RoHS - Restriction of Use of Hazardous Substances
C.	WEEE - Waste Electrical and Electronic Equipment Directive
D.	RFC - Request for Comments
E.	IEEE - Institute of Electrical and Electronics Engineers
F.	EN/IEC - International Electrotechnical Commission

1.04	SYSTEM DESCRIPTION
A.	Connection Requirements: Provides two RJ45 connections.
1.	The system shall utilize Category 5/5e/6 cables terminated in RJ45 connector with EIA568-B configuration for PoE and data in for standard 10Base-T or 100Base-T.

1.05	SUBMITTALS
A.	Manufacturer’s Installation and Operating Manual: Printed Installation and Operating Information
B.	Warranty: Manufacturer’s Printed Warranty

1.06	DELIVERY, STORAGE AND HANDLING
A.	Store in original packaging in a climate-controlled environment.
B.	Storage temperature not to exceed: -40˚C to +85˚C

1.07	PROJECT/SITE CONDITIONS
A.	Temperature Requirements: Product shall operate in an environment with an ambient temperature range of -20˚C to +70˚C without the assistance of fan-forced cooling.
B.	Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). 

1.08	WARRANTY
A.	Limited Lifetime Warranty: Vigitron guarantees product to be free of defects for product’s lifetime, defined as the time that product is in production plus 3 years from the end of production.

PART 2 - PRODUCTS
2.1	MANUFACTURER
A.	Acceptable Manufacturer: 
1.	Vigitron, Inc. 7810 Trade Street, Suite 100, San Diego, CA 92121 USA 
2.	Phone: 1-858-484-5209
3.	Email: support@vigitron.com
B.	Substitutions: Not Permitted

2.2	MANUFACTURED UNITS
A.	Reference Table A: Product Number, Descriptions and Maximum Distance
B.	Reference Table B: IEEE Product Compatibility Chart
C.	Reference Table C: Product System Compatibility Chart

2.3	GENERAL SPECIFICATIONS
A.	The Ethernet and PoE repeater shall be Vi3002.
B.	Ethernet Port:
1.	The device shall support the Ethernet data IEEE 802.3/802.3u 10/100Base-TX protocol.
2.	Bandwidth will be automatically detected and set at 10Mbps or 100Mbps.
3.	The device features two 10/100TX Ethernet ports in a compact mini chassis.
The Ethernet port will comply with:
i.	IEEE 802.3 10BaseT 
ii.	IEEE 802.3u 100Base-T 
4.	All ports will be compliant to IEC 60603-7.
5.	The device shall support standard Ethernet transmission at distances up to 100m.
6.	The device will comply for insertion in 3, 3 ½, and 4 inch conduit as for 2002 NEC standards for max fill at 40%.
C.	The Vi3002 will be able to support IEEE 802.3af/at/bt up to 60W.
D.	The device will maintain all 802.3 PoE safety standards for PSE and PD communications.
E.	The device will have the ability to be powered from and pass through PoE sources compliant to IEEE 802.3af/at/bt up to 60W.
F.	The device will consume less than 1.0W of power by a PoE source.
G.	The device shall provide indicating LED’s for monitoring proper system operation.
1.	PoE Power: Green LEDs with both sides of the RJ45 connector on.
2.	Standard Ethernet Traffic Connection
a.	Off – No Traffic
b.	On – Traffic Present

2.4	DATA SPECIFICATIONS
A.	Data Interface: Passage of data compliant to: 
1.	RFC 768 UDP
2.	RFC 2068 HTTP
3.	RFC 793 TCP
4.	RFC 791 IP
5.	RFC 1783 TFTP
6.	RFC 894 IP over Ethernet
7.	RFC 2544 TCP/IP Packet Transmission
B.	Data Rate: 10/100Mbps
C.	Data Inputs: 2
1.	Two RJ45 conforming to IEC 60603-7
2.5	Vi3002 SPECIFICATIONS and FEATURE SETS
A.	Repeater will be able to provide the following performance: 
1.	Bandwidth per device will be constant over the quoted extended distance with less than a one percent (1%) decrease.
2.	Latency per device will be no greater than 9.0us. 
B.	Packet losses per device will be less than one percent (1%) at 1,518 bytes packet sizes.
C.	Packets per second (PPS) loss per device will be less than 1%.
D.	Unit will function as a Layer 2 network switch with the following features:
1.	MDI-MDIX support
2.	IP DiffServ
3.	Port-based QoS
4.	Broadcast Storm Protection
E.	The device will support the ability to pass 802.3af/at/bt PoE from a source to a device at the stated distances to provide power to a PD device.
F.	Extender must have the ability to operate using Pass-Through-PoE (PTP^TM) with a PSE source that provides power to all devices over a UTP Category cable.
G.	Vi3002 must have the ability to Pass-Through-PoE functionality in compliance to IEEE 802.3af/at/bt standards when communicating with a PD device.
1.	Pass through detection pulses from PSE to PD.
2.	Pass through classification pulses from PSE to PD.
3.	Pass through required power from PSE to PD 
H.	The device must be able to operate in extended temperate environments of -20˚C to 75˚C.
I.	The device must provide the ability to test transmission connection continuity and bandwidth by means of LED indicators.

2.6	CONNECTORS
A.	Standard Transmission RJ45 Port conforming to IEC 60603-7  

2.7	ELECTRICAL SPECIFICATIONS
A.	Power Inputs: PoE power sources up to 60W. Device uses 1.0W max.

2.8	MECHANICAL SPECIFICATIONS
A.	Dimensions: 0.9 x 1.0 x 3.39 in, 2.3 x 2.5 x 8.6 cm (HxWxL) (no tab size)
B.	Material: Device shall be constructed of an Aluminum enclosure.
C.	Weight: 0.01 lb, (45g)

2.9	ENVIRONMENTAL SPECIFICATIONS 
A.	Operating Temp: -20˚C to +75˚C 
B.	Storage Temp: -40˚C to +85˚C
C.	Relative Humidity: 0% to 95% (Non-condensing)

2.10	REGULATORY AGENCIES/APPROVALS AND LISTINGS 
A.	FCC Part 15, Subpart B, Class B 2010
B.	Emission Standards: 
1.	EN 5502:2006+A1:2007
2.	EN 61000-3-3:2008
3.	EN 61000-3-2:2006+A1:2009+A2:2009
4.	EN 55024:1998+A1:2001+A2:2003
C.	RoHS
D.	CE
E.	WEEE

2.11	MANUFACTURED UNIT REFERENCE TABLES

Table A: Product Number Descriptions
PRODUCT | DESCRIPTION | MAX. DISTANCE*
Vi3002 | Ethernet Data and PoE Repeater | 328 Feet (100m) @ 10/100Base-T
* Distance represents single device link.

Table B: Product IEEE Compatibility Chart
PRODUCT | | COMPATIBLE IEEE STANDARDS

Vi3002

IEEE 802.3u     IEEE 802.3af      
IEEE 802.3at  
IEEE 802.3bt

Fast Ethernet standard for 10/100TX
Power over Ethernet
Power over Ethernet
Power over Ethernet

Vigitron reserves the right to change products or specifications without notice.

END OF SECTION