Author: ali

DIVISION 27 21 29
Vi10480 Hardened 480W, 56VDC Din Rail Mount Power Supply 
PART 1 - GENERAL
1.01	SUMMARY 
A.	Hardened 480W 56VDC Din Rail Mount Power Supply 

1.02	SECTION INCLUDES
A.	Vi10480, 480W Hardened Din Rail Power Supply 

1.03	REFERENCES
A.	CE - European Union Compliance (CE)
B.	RoHS - Restriction of Use of Hazardous Substances
C.	WEEE - Waste Electrical and Electronic Equipment Directive 
D.	UL - Underwriters Laboratory
E.	RFC - Request for Comments
F.	IEEE - Institute of Electrical and Electronics Engineers
G.	EN/IEC - International Electrotechnical Commission

1.04	SYSTEM DESCRIPTION
A.	Connection Requirements: Terminal blocks for AC input, DC output, Parallel input and Status relay output
B.	Wire between 10-20AWG solid wire will be allowed for all connections. 
C.	Power supply is used to provide DC power to devices providing PoE 

1.05	SUBMITTALS
A.	Manufacturer’s Installation and Operating Manual: Printed installation and operating information
B.	Warranty: Manufacturer’s Printed Warranty

1.06	DELIVERY, STORAGE AND HANDLING
A.	Store in original packaging in a climate controlled environment.
B.	Storage Temperature not to exceed: -40˚C to +85˚C

1.07	PROJECT/SITE CONDITIONS
A.	Temperature Requirements: Product shall operate in an environment with an ambient temperature range of -25˚C to +70˚C without the assistance of fan-forced cooling.
B.	Humidity Requirements: Products shall operate in an environment with relative humidity of 20% to 90% (non-condensing). 

1.08	WARRANTY
A.	Limited Life Time Warranty: Vigitron guarantees product to be free of defects for product’s lifetime, defined as the time that product is in production plus 3 years from the end of production.

PART 2 - PRODUCTS
2.1	MANUFACTURER
A.	Acceptable Manufacturer: 
1.	Vigitron, Inc. 7810 Trade Street, Suite 100, San Diego, CA 92129, USA 
2.	Phone: 1-858-484-5209
3.	Email: support@vigitron.com
B.	Substitutions: Not Permitted

2.2	MANUFACTURED UNITS
A.	Reference Table A: Product Number and Descriptions 

2.3	GENERAL SPECIFICATIONS
A.	The power supply shall be Vi10480.
B.	The power supply will have an efficiency up to 92%.
C.	The power supply will have a peak capacity load of 150% to 720W.
D.	The power supply will have an over load of up to 150% of rated current. 
E.	Recovery from over current will result in the power supply stop working after 7 seconds and monitor for restart after 7 seconds.
F.	The power supply will have auto recovery after power shutdown.
G.	The power supply will be able to operate within a temperature range of -25˚C to +70˚C.
H.	Can be installed on Din Rail mounts for TS-35/7.5 and TS-35/15 standards.  
I.	Short Time operations will provide 11A at 70˚C.
J.	Continuous operations will provide 8A at 70˚C.

2.4	SPECIFICATIONS and FEATURE SET
A.	Built in DC relay contact
B.	Universal AC input range (85~350VAC)
C.	Ability to provide redundant power by connecting two units in parallel 
D.	Ability to increase power by adding additional power supplies in parallel 
E.	Built-in active PFC,PF>0.95
F.	Built-in current sharing function
G.	Built-in current limiting circuit
H.	Output protections: OVP/OLP/SCP/OTP
I.	150%(720W) peak load capacity
J.	Fuse Tripping due to High Overload Current with reset
K.	Built-in DC OK relay contact
L.	Output Specifications
1.	Voltage ADJ Accuracy		+/-3.0%
2.	Line Regulation 			+/-0.5%
3.	Load Regulation 			+/-1.0%
4.	Set up Time 100-120VAC		<500ms
5.	Set up time 230VAC		<3s@230VAC
6.	Hold up Time 			>/=20ms @ full load 230VAC 
7.	Temperature Coefficient 		+/-0.03%/C 
8.	Overshoot and Undershoot 		<5.0%
M.	Input Specifications 
1.	Voltage Range 			85VAC-264VAC, 130VDC-350VDC
2.	Frequency Range			47Hz-63Hz
3.	Typical Power Factor 		0.99 @ 110VAC, 0.95/230 VAC
4.	Typical Efficiency 			93.8% 
5.	Max. AC Current 			<7A/100VAC, 3.5A/230VAC
6.	Typical Inrush Current		<20A/110VA, <40A/230VAC Cold Start 
7.	Leakage Current 			Input to output <0.25mA, input PG <3.5mA
N.	Protection
1.	Over Load				Max 150% of rated current. Stop work after 7
	seconds, restart after 7 seconds from shut down 
2.	Over Voltage			58-63VDC 
3.	Over Temperature 			115°C internal auto shut down and recover
4.	Short Circuit 			Long term sensing with auto recover

2.5	CONNECTORS
A.	AC Power: 3-pin Terminal Block
1.	Terminal 1: L 
2.	Terminal 2: N
3.	Terminal 3: PG 
B.	DC Relay:  
1.	Terminal 1: DC Relay Contact 
2.	Terminal 2: OK Relay Contact
C.	DC power output: 
1.	Terminal 3: +V
2.	Terminal 4: +V
3.	Terminal 5: +V
4.	Terminal 6: -V
5.	Terminal 7: -V
6.	Terminal 8: -V

2.6	MECHANICAL SPECIFICATIONS
A.	Dimensions: 5 x 2.8 x 4.9in / 127 x 70 x 124mm (L x W x H)
B.	Finish:  sheet metal
C.	Weight: 2.54 lbs (1.15kg)

2.7	ENVIRONMENTAL SPECIFICATIONS
A.	Operating Temp: -25˚C to +70˚C
B.	Storage Temp: -40˚C to +85˚C
C.	Relative Humidity: 5% to 95% (non-condensing)

2.8 REGULATORY AGENCIES/APPROVALS AND LISTINGS
A.	FCC Part 15, Subpart B, Class B 
B.	Emission Standards: 
1.	EN 55022: EN 55024
2.	EN61000-4-2,3,4,5,6,8,11- heavy industry level 
C.	Safety:
1.	UK 508, UL 60950, EN60950, CE 
D.	Environmental:
1.	RoHS
2.	WEEE

2.9 ACCESSORIES
A.	Operation Manual

2.10 MANUFACTURED UNITS REFERENCE TABLES

PRODUCT | DESCRIPTION
Vi10480 | 480W, 56VDC -Hardened DIN Rail Power Supply
Table A: Product Number Descriptions

Vigitron reserves the right to change products or specifications without notice.

END OF SECTION