Title: Vi1304VPD A&E Spec
Author: SW
Last saved by: Steve
Company: Vigitron
Document comments: Specification most similar to

Unshielded Twisted-Pair Video, Power & Data Combiner
Architecture and Engineering Bid Specification
Page  Vigitron Vi1304VPD or equivalent

TECHNICAL SPECIFICATIONS                                                   		SECURITY SYSTEM
DIVISION 16 - ELECTRICAL
SECTION 16770 - CLOSED CIRCUIT TELEVISION (CCTV) SYSTEM/ Cable Transmission and Reception Equipment

PART 2 – PRODUCTS                 

2.1	 GENERAL

A.	All equipment shall be standard components that are regularly manufactured and available.

B.	All systems and components shall have been tested and verified in actual use.

C.	All equipment shall be provided with the availability of a U.S.A toll-free technical support number from the manufacturer. The number shall provide technical assistance to the caller at no charge for as long as the product is installed.

2.2	UNSHIELDED TWISTED PAIR-VIDEO, POWER & DATA COMBINER

A.	The UTP Passive Video-Power-Data Combiner shall be capable of accepting four Video, Power and Data signals via RJ45 Jacks using CAT5. The Combiner shall not  require power. 

B.	The device shall act as a combiner in that it shall be used to connection point for Video, Power and Data signals. It shall connect using an RJ-45 Jack, which will accept an RJ-45 plug wired to CAT5 or better unshielded twisted pair cable. The receptacle shall be wired so that one twisted pair is designated for video transmission to and from the transceiver device, one twisted pair may be used for transmission of RS422/485 control signals and two twisted pairs may be used to provide operational power to the camera.

C.	Bi-directional signal transmission via the Vertical Interval of the video signal shall be supported up to 750 feet (229 m) when using this device to transmit the signal to another passive receiver, so long as all other requirements are met. These signals are typically known as “Up the Coax” control, used to facilitate Pan/Tilt/Zoom functionality with the appropriate and compatible PTZ hardware.

D.	The Combiner enclosure shall be equipped with a single RJ45 jack designated for Data connection via Unshielded Twisted Pair wire.

E.	The Combiner shall be equipped with four RJ-45s jack for connection to remote camera locations via CAT5 or better cable. 

F.	Each RJ-45 connector has a power LED. Each power input has a 1 Amp resetable fuse

G.	The combiner shall meet or exceed the following performance specifications:
a.	Typical common-mode rejection of 60 dB between the frequencies of 15 KHz-5 MHz.
b.	The receiver device shall be compatible with NTSC, PAL and SECAM color video standards.
c.	Compatible with 0.6 to 1.6 Vpp composite color or black and white video signals into 75 Ohms.
d.	Frequency response from DC to 6 MHz.
e.	Typical Insertion Loss of 0.5 dB or less. 

H.	The combiner shall be suitable for indoor use or for outdoor use in an environmental enclosure at an operating temperature range of –20 to 75 degrees Celsius. 

I.	The combiner shall be compatible with Category 2 or better UTP wire as specified in this document

J.	The combiner shall weigh no more than 0.2 lbs or 90 g

K.	The combiner dimensions shall not exceed 1.75" x 1.0" x  4.88"(44.5mm x 25.4mm x 124 mm)

B.	The receiving device shall be able to be front mounted in a 1U 19” rack space or wall/table mountable . Up to three receiving devices shall fit on a 1U 19” rack space, available optionally.

L.	The combiner shall be UL/cUL listed, and CE Compliant.

M.	The combiner manufacturer shall provide a limited lifetime warranty.

N.	The UTP Video-Power-Data combiner shall be the:
a.	Vigitron Vi1304VPD or
b.	Equivalent product