Title: Vi1216VPD A&E Spec
Author: SW
Last saved by: Ali Eghbal
Company: Vigitron

16-CH Powered UTP Combiner Hub
Architecture and Engineering Bid Specification
Page  Vigitron Vi1416VPD or equivalent

TECHNICAL SPECIFICATIONS                                                   		SECURITY SYSTEM
DIVISION 16 - ELECTRICAL
SECTION 16770 - CLOSED CIRCUIT TELEVISION (CCTV) SYSTEM/ Cable Transmission and Reception Equipment

PART 2 – PRODUCTS                 

2.1	 GENERAL

A.	All equipment shall be standard components that are regularly manufactured and available.

B.	All systems and components shall have been tested and verified in actual use.

C.	All equipment shall be provided with the availability of a toll-free (U.S. and Canada) technical support number from the manufacturer. The number shall provide technical assistance to the caller at no charge for as long as the product is installed.

2.2	16-CHANNEL POWERED UTP COMBINER HUB

A.	Shall act as a combiner in that it shall be used as the connection point for video-power-data to and from cameras via one Rj-45 connector per camera for up to 16 cameras. 

B.	Shall connect to each camera using an RJ-45 Jack and via a CAT2 or better unshielded twisted pair cable. The RJ-45 connector shall be wired so that one twisted pair is designated for video transmission from the transceiver device, one twisted pair may be used for transmission of RS422/485 control signals and two twisted pairs may be used to provide operational power to the camera.

C.	Shall be equipped with an RJ-45 jacks for connection to UTP wire for each camera.

D.	Shall deliver signals operating in the same cable bundle as telephone, data, low voltage or other video signals, without interference. 

E.	Shall be able to accept 24-16 AWG UTP wires via RJ-45 connectors.

F.	Shall be compatible with a video-power-data transceiver at each camera end and comply with standard structured cabling pin-outs of RJ45 per EIA/TIA 568B as following:
Pin#         Signal
  1           + Video
  2            - Video
  3           + Data
  4            - Power
  5            + Power
  6            - Data
  7            + Power
  8            - Power

G.	Shall be equipped with four RJ-45 connectors designated for Data connection via Unshielded Twisted Pair wires.  There will be a dedicated pair available for each camera deliver Pan/Tilt/Zoom telemetry signals from the control room to the cameras.  Data connection pin-outs shall be:
Camera 1-4 RJ45 Connector
Pin#         Signal        Camera
  1           + Data               1
  2            - Data               1
  3           + Data               2
  4            - Data               3
  5            + Data              3
  6            - Data               2
  7            + Data              4
  8            - Data               4

Camera 5-8 RJ45 Connector
Pin#         Signal        Camera
  1           + Data               5
  2            - Data               5
  3           + Data               6
  4            - Data               7
  5            + Data              7
  6            - Data               6
  7            + Data              8
  8            - Data               8

Camera 9-12 RJ45 Connector
Pin#         Signal        Camera
  1           + Data               9
  2            - Data               9
  3           + Data               10
  4            - Data               11
  5            + Data              11
  6            - Data               10
  7            + Data              12
  8            - Data               12

Camera 13-16 RJ45 Connector
Pin#         Signal        Camera
  1           + Data               13
  2            - Data               13
  3           + Data               14
  4            - Data               15
  5            + Data              15
  6            - Data               14
  7            + Data              16
  8            - Data               16

H.	Shall provide a fully isolated (floating) Class 2 24/28VAC camera power ensuring total ground-loop immunity, pass-through video, and telemetry data connectivity for up to 16 cameras over a single RJ45 4-pair UTP cable per camera.

I.	Shall provide up to 1 Amp per channel, 12 Amps aggregate.

J.	Shall have independent diagnostic LEDS per-channel, one fuse status LED and one load/no-load diagnostic LED as follows:
Red LED off = Fuse blown
Red LED on = Fuse OK
Green LED Off = No load connected
Green LED On = Load connected

K.	Shall provide a 2A glass fuse for each camera power output easily accessible from front panel. 

L.	Shall be compatible with Category 2 or better UTP wires.

M.	Shall have an individually selectable output (24VAC-OFF-28VAC) per camera connection.

N.	Shall be powered by 115/230 VAC 50/60 Hz, selectable via an external switch.

O.	Shall have a current draw of up to 4.8 Amps at 115 VAC or 2.4 Amps (230 VAC) when under full load.

P.	Shall have protection of 5Amp slow-blow 5X20mm fuse & thermal shutdown fuse.

Q.	Shall have a power rating of 360 Watts.

R.	Shall require a minimum airflow of 5 ft^3/min (0.135 m^3/min).

S.	Shall operate with ambient temperature range of 0 to + 140 ºF (-20 to + 50 ºC)

T.	Shall operate within humidity (non-condensing) of 1 to 95%.

U.	Shall weigh no more than 22 lbs (10 Kg).
V.	Shall have all the connectors on the rear.
W.	The dimensions shall not exceed 1.75 x 17 x 12 Inches, 4.3 x 43 x 30.5 cm (H x W x L). 
X.	Shall be able to be front or rear mounted in a 1U 19” rack space or wall/table mountable. 
Y.	Shall include sixteen 2-foot (60 cm) coax patch cables
Z.	Shall be UL/cUL listed, and CE Compliant.
AA.	Y. Shall be RoHs compliant.
BB.	Z. Shall be WEEE compliant
CC.	Shall be provided with a limited lifetime warranty.
DD.	Shall be the Vi1416VPD or approved equivalent product