TECHNICAL SPECIFICATIONS                                                   		SECURITY SYSTEM
DIVISION 16 - ELECTRICAL
SECTION 16770 - CLOSED CIRCUIT TELEVISION (CCTV) SYSTEM/ Cable Transmission and Reception Equipment

PART 2 – PRODUCTS                 

2.1	 GENERAL

A.	All equipment shall be standard components that are regularly manufactured and available.

B.	All systems and components shall have been tested and verified in actual use.

C.	All equipment shall be provided with the availability of a U.S.A toll-free technical support number from the manufacturer. The number shall provide technical assistance to the caller at no charge for as long as the product is installed.

2.2	UNSHIELDED TWISTED-PAIR ACTIVE MULTI-CHANNEL VIDEO RECEIVER

A.	The UTP Active Video Receiver Hub shall be capable receiving sixteen baseband monochrome or color video signals over unshielded twisted-pair (UTP) telephone wire from a passive transceiver up to a distance of 3,500 feet (1,060 m). Distances up to 6,000 feet (1,830 m) shall be supported when used in conjunction with an amplified (active) transmitter for NTSC & PAL video signals using Category 5 cable.

B.	The receiving device shall have fully automatic (no adjustment) digital video compensation for each port, within distance specified for NTSC and PAL standards. The receiver shall continuously analyze incoming video signal and automatically compensate for cable attenuation independent of video signal content.
C.	The Receiver Hub shall have an integrated Video Distribution Amplifier, with four BNC outputs per channel.

D.	The receiving device shall deliver a baseband video signal capable of driving a 75-ohm load.

E.	The Receiver shall have integrated differential transient protection without the need for a ground connection. Additionally, the transceiver shall have integrated common mode transient protection, which to be functional, requires an electrical ground connection via screw terminal.

F.	The Receiver shall be equipped with corrosion-resistant screw terminals for connection to UTP wire.

G.	A pair of removable terminal blocks shall be provided for connection of each port to UTP wire.

H.	The receiving device shall be powered by 110-240 Volts AC.

I.	The receiving device shall have a Red “Power-On” LED.

J.	The Receiver shall have a Green "Video Present" LED for each channel to indicate accurate reception of minimum sync level for stable video signals.

K.	The receiving device shall have built-in ground lifting.

L.	The receiver shall deliver signals operating in the same cable bundle as telephone, data, low voltage or other video signals, without interference.

M.	The receiver shall meet or exceed the following performance specifications:
a.	Typical common-mode rejection of 70 dB between the frequencies of 15 KHz-5 MHz.
b.	The receiver device shall be compatible with NTSC, PAL and SECAM color video standards.
c.	Compatible with 0.6 to 1.6 Vpp composite color or black and white video signals into 75 Ohms.
d.	Frequency response from DC to 6 MHz.
e.	Transient immunity of 6,000V 1.2uS x 50 uS and 3,000A 8uS x 20 uS when ground screw terminal is bonded to earth ground per IEEE Std C62.41, formerly known as IEEE Std 587 (IEEE Recommended Practice for Surge Voltages in Low-Voltage AC Power Circuits). 
f.	The receiver shall be suitable for indoor use or for outdoor use in an environmental enclosure at an operating temperature range of 0 to 50 degrees Celsius. 

N.	The receiver shall be compatible with 24-16 AWG UTP wire.

O.	The receiver shall be compatible with Category 2 or better UTP wire, except as otherwise specified in this document. 

P.	The receiver shall weigh no more than 3.5 Lbs (1.6kg).

Q.	The receiver dimensions shall not exceed 17", 1.7", 8.0" (43 cm, 4.3 cm, 20.3 cm).

R.	The receiving device shall be able to be packaged with a Rack Kit, to support front mounting in a 1U 19” rack space or wall/table mounting. Rubber feet shall be included to support desk mount applications.

S.	The receiver shall include sixteen 2-foot (60 cm) coax patch cables

T.	The receiver shall be UL/cUL listed, and CE Compliant.

U.	The receiver manufacturer shall provide a limited lifetime warranty.

V.	The UTP active video receiver shall be the:
a.	Vigitron Vi6316 or
b.	Equivalent product

TECHNICAL SPECIFICATIONS                                                   		SECURITY SYSTEM
DIVISION 16 - ELECTRICAL
SECTION 16770 - CLOSED CIRCUIT TELEVISION (CCTV) SYSTEM/ Cable Transmission and Reception Equipment

PART 2 – PRODUCTS                 

2.1	 GENERAL

A.	All equipment shall be standard components that are regularly manufactured and available.

B.	All systems and components shall have been tested and verified in actual use.

C.	All equipment shall be provided with the availability of a U.S.A toll-free technical support number from the manufacturer. The number shall provide technical assistance to the caller at no charge for as long as the product is installed.

2.2	UNSHIELDED TWISTED-PAIR ACTIVE MULTI-CHANNEL VIDEO RECEIVER

A.	The UTP Active Video Receiver Hub shall be capable receiving sixteen baseband monochrome or color video signals over unshielded twisted-pair (UTP) telephone wire from a passive transceiver up to a distance of 3,500 feet (1,060 m). Distances up to 6,000 feet (1,830 m) shall be supported when used in conjunction with an amplified (active) transmitter for NTSC & PAL video signals using Category 5 cable.

B.	The receiving device shall have fully automatic (no adjustment) digital video compensation for each port, within distance specified for NTSC and PAL standards. The receiver shall continuously analyze incoming video signal and automatically compensate for cable attenuation independent of video signal content.
C.	The Receiver Hub shall have an integrated Video Distribution Amplifier, with two BNC outputs per channel.

D.	The receiving device shall deliver a baseband video signal capable of driving a 75-ohm load.

E.	The Receiver shall have integrated differential transient protection without the need for a ground connection. Additionally, the transceiver shall have integrated common mode transient protection, which to be functional, requires an electrical ground connection via screw terminal.

F.	The Receiver shall be equipped with four RJ-45 Ports for connection to UTP wire.

G.	The receiving device shall be powered by 110-240 Volts AC.

H.	The receiving device shall have a Red “Power-On” LED.

I.	The Receiver shall have a Green "Video Present" LED for each channel to indicate accurate reception of minimum sync level for stable video signals.

J.	The receiving device shall have built-in ground lifting.

K.	The receiver shall deliver signals operating in the same cable bundle as telephone, data, low voltage or other video signals, without interference.

L.	The receiver shall meet or exceed the following performance specifications:
a.	Typical common-mode rejection of 70 dB between the frequencies of 15 KHz-5 MHz.
b.	The receiver device shall be compatible with NTSC, PAL and SECAM color video standards.
c.	Compatible with 0.6 to 1.6 Vpp composite color or black and white video signals into 75 Ohms.
d.	Frequency response from DC to 6 MHz.
e.	Transient immunity of 6,000V 1.2uS x 50 uS and 3,000A 8uS x 20 uS when ground screw terminal is bonded to earth ground per IEEE Std C62.41, formerly known as IEEE Std 587 (IEEE Recommended Practice for Surge Voltages in Low-Voltage AC Power Circuits). 
f.	The receiver shall be suitable for indoor use or for outdoor use in an environmental enclosure at an operating temperature range of 0 to 50 degrees Celsius. 

M.	The receiver shall be compatible with 24-16 AWG UTP wire.

N.	The receiver shall be compatible with Category 2 or better UTP wire, except as otherwise specified in this document. 

O.	The receiver shall weigh no more than 3.5 Lbs (1.6kg).

P.	The receiver dimensions shall not exceed 17", 1.7", 8.0" (43 cm, 4.3 cm, 20.3 cm).

Q.	The receiving device shall be able to be packaged with a Rack Kit, to support front mounting in a 1U 19” rack space or wall/table mounting. Rubber feet shall be included to support desk mount applications.

R.	The receiver shall include Sixteen 2-foot (60 cm) coax patch cables

S.	The receiver shall be UL/cUL listed, and CE Compliant.

T.	The receiver manufacturer shall provide a limited lifetime warranty.

U.	The UTP active video receiver shall be the:
a.	Vigitron Vi6316-J or
b.	Equivalent product