DIVISION 27 21 29
Vi30210 8 + 2 L2+, 90W Industrial Managed Network Switch 
PART 1 - GENERAL
1.1	SUMMARY
A.	8 + 2, L2+ Managed 90W managed industrial network switch   

1.2	SECTION INCLUDES
A.	Vi30210 8 + 2 -port PoE powered PoE Network Switch  

1.3	REFERENCES
A.	European Union Compliance (CE)
B.	Rohs
C.	WEEE 
D.	UL – Underwriters Laboratory 
E.	FCC

1.4	SYSTEM DESCRIPTION
A.	Performance Requirements: Provide 8 ports for network switching and PoE, two combination ports for copper and fiber with an external power source. 
B.	The system shall utilize TIA/EIA 568-B cable connected to an RJ-45 plug. 

1.5	SUBMITTALS
A.	Manufacturer’s Installation and Operation Manual: Printed Installation and Operation Information
B.	Warranty: Manufacturer’s Printed Warranty

1.6	DELIVERY, STORAGE AND HANDLING
A.	Store in original packaging in a climate-controlled environment. 
B.	Storage temperature not to exceed: -40˚C to +85˚C

1.7	PROJECT/SITE CONDITIONS
A.	Temperature Requirements: Product shall operate in an environment with an ambient temperature range of -40˚C to +75˚C without the use of internal fans.
B.	Cold Start will be -40˚C
C.	Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 90% (non-condensing). 

1.8	WARRANTY
A.	Limited Lifetime Warranty: Vigitron guarantees product to be free of defects for product lifetime, defined as the time that product is in production plus 3 years from end of production.

PART 2 - PRODUCTS
2.01	MANUFACTURER
A.	Acceptable Manufacturer: 
1.	Vigitron, Inc.: 7810 Trade Street Suite 100, San Diego, CA 92121, USA 
2.	Phone: +1 (858) 484-5209
3.	Email: support@vigitron.com
B.	Substitutions: Not Permitted

2.02	MANUFACTURED UNITS
A.	Reference Table A: Compatible ANSI/IEEE Standards 
B.	Reference Table B: Compatible Ethernet Equipment

2.03	GENERAL SPECIFICATIONS
A.	The switch will contain 10 active copper ports.
B.	Eight copper ports will provide PoE 
C.	Two combination copper and fiber ports will be used as uplinks 
D.	All ports will automatically detect network speeds of 100Mbps, 1,000Mbps and 2,500Mbps.
E.	Copper ports will support network speeds up to 1,000Mbps  
F.	Fiber ports will support network speeds up to 2,500Mbps 
G.	The switch will support internal bandwidth up to ,500Mbps.
H.	The switch will be model Vi30210
I.	Standard Ethernet Ports:
1.	The device shall have 10 standard Ethernet ports and 2 SFP port in a compact housing. The Ethernet port shall comply with: 
a.	IEEE 802.3u 100BaseT 
b.	IEEE 802.3az 1,000BaseT 
c.	IEEE 802.3bz 2,500BaseT
2.	The SFP ports will comply with MSA standards.
3.	The standard ports of device shall support standard Ethernet UTP connection with distances up to 100m.
4.	The SFP port will be set at 100/1,000/2,500Mbps.
J.	Port bandwidth settings will be done by automatically.
K.	Port PoE can be up to 90W IEEE 802.3bt compliant 
L.	Port PoE allocations will be done automatically depending on port power requirements.
M.	The switch will be powered by an external power supply up to 495W. 
1.	The maximum port power will be 90W 
N.	The Switch will provide for dual inputs.
1.	Each power input will serve as a redundant input. 
O.	Each power input will serve as a redundant input. 
P.	The switch will have built-in smart PoE power allocation providing the required PoE powered devices up to 90W per port. 	
Q.	The switch will have programmable per port thermal protection up to 125˚C, shutting down when temperature is exceeded,  
R.	The switch will have 6kV surge per port surge protection. 
S.	The switch will have two alarm inputs
T.	The switch will have two alarm outputs: 
1.	Each will be programmable as Form C, N/O, N/C 
U.	The switch fill will provide for Rapid Ring features compliant to: 
1.	G.8032V1
2.	G.8032V2

2.04	DATA SPECIFICATIONS
A.	Data Interface: Passage of Data Compliant to:
1.	RFC 768 UDP
2.	RFC 2068 HTTP
3.	RFC 793 TCP
4.	RFC 791 IP
5.	RFC 1783 TFTP
6.	RFC 894 IP over Ethernet
7.	RFC 2544 TCP/IP Packet Transmission
B.	Port Data Rate: 100/1000/2500Mbps
C.	Packet handling up to 9600 bytes
D.	Data Connections: 
1.	10 Standard Ethernet Ports
2.	2 SFP Fiber ports 
D.	Port PoE Power Outputs: 
1.	15.4W compliant to IEEE802.3af 
2.	30W complaint to IEEE802.3at, Type 1 and Type 2
3.	Up to 90W Compliant to IEEE802.3bt standards 
 E. The DC input connector will be a pluggable terminal block

2.05	SPECIFICATIONS AND FEATURE SETS
A.	The Vi30210 transmits and receives data. 
1.	Internal bandwidth will be constant with no more than a 2% decrease, when the input signal varies from a size of 64 bytes to 9,600 bytes using bidirectional transmission. 
2.	Internal bandwidth will be constant over the quoted extended distance with no more than 2% decrease when: 
a.	Bidirectional signals are transmitted with a packet size of 9,600 bytes.
b.	Unidirectional signals are transmitted with a packet size of 9,600 bytes.
c.	Bandwidth will remain the same for both upload and download operation.
B.	Packet losses will be at 2% or less at packet sizes, ranging from 64 bytes to 9,600 bytes bidirectional unidirectional at 2,500Mbps.
C.	Packets per second (PPS) will not vary more than 2% at packet sizes, ranging from 64 bytes to 9,600 bytes bidirectional transmission. 
D.	Maximum distance from switch port to device will be 328 ft. (100m) for data and PoE.
E.	The switch will be compliant with IEEE 802.3az as detailed in the Energy Efficient Ethernet Task. It has the ability to automatically turn off PoE when link down is detected and/or idle, and resume without packet loss when link up is detected. 
F.	Each port will be continuously monitored for potential overcurrent and thermal conditions. 
G.	The device must have the ability for PoE functionality in compliance with IEEE 802.3af/at/bt standards when communicating with a PD: 
1.	Will provide detection pulses to PD.
2.	Will provide Classification pulses to PD and report via GUI. 
3.	Will provide IEEE802.3af/at/bt, Class 0 to Class 8 PoE power to PD, depending on the external power supply. 
4.	Will provide up to 90W per port PoE power. 
5.	Will provide auto-sensing for connected devices and individual port power up to 90W.
6.	Will programming PoE delay up to 600 seconds  
H.	The switch will provide for locking specific MAC addresses to specific ports, while user programming will limit the number of allowed 1K MAC addresses per port. 
I.	The switch will allow firmware updates via HTTP/HTTPs and TFTP, in addition to directly via an on-board console port.
J.	The switch will support IEEE 802.1Q.
K.	Power consumption will be 12.3W for basic switch functions.

L.	Time and Date can be set using: 
1.	NTP reference to an NTP 
2.	RTC (Real Time Clock) 
i.	Both clocks will have internal time day settings 
ii.	Clock will have 12 or 24 hours setting
iii.	Date format will have the following option:
1.	mm/dd/yyyy
2.	mm/yyyy/dd
3.	yyyyy/dd/mm

2.06	CONNECTORS
A.	Power Inlet: Pluggable Terminal Block 
B.	Alarm input: Pluggable Terminal Block 
C.	Alarm output: Pluggable Terminal Block 
D.	Standard Ethernet: RJ-45, IEC 60603-7
E.	Fiber: MSA Compliant 

2.07	ELECTRICAL SPECIFICATIONS
A.	External Power Supply:
1.	Up to 495W @ 57VDC
B.	PoE Output Power (depending on external power supply):
1.	15.4W compliant to IEEE802.3af 
2.	30W complaint to IEEE802.3at, Type 1 and Type 2
3.	Up to 90W Compliant to IEEE802.3bt standards 

2.08	MECHANICAL SPECIFICATIONS 
A.	Dimensions (H x W x L): 2.6 x 6 x 4.4 inches (5 x 16.8 x 11 cm)  
B.	Finish: Device shall be constructed of a metal enclosure. 
C.	Weight: 1.9lb (862 g) 

2.09	ENVIRONMENTAL SPECIFICATIONS
A.	Operating Temperature: -40˚C to +70˚C at 240W 
B.	Operating Temperature: -40˚C to +55˚C at 480W
C.	Cold Start -40˚C
D.	Storage Temperature: -40˚C to +85˚C
E.	Relative Humidity: 0% to 95% (non-condensing)

2.10	REGULATORY AGENCIES/APPROVALS AND LISTINGS
A.	FCC Part 15, Subpart A
B.	Emission Standards: 
1.	FCC Part 15, Subpart B, Class A
2.	EN 55022:2006+A1:2007
3.	EN 61000-3-2:2006+A1:2009+A2:2009
4.	EN 61000-3-3:2008
5.	EN 55024:1998+A1:2001+A2:2003
6.	EN55032
7.	EN55035
8.	EN50121
9.	EN50155
C.	RoHS

D.	Environmental:
1.	EN 62368 (Replacing EN60950-1) 
2.	IEC60068-2-27 (Shock) 
3.	IEC60068-2-32 (Free Fall) 
4.	IEC60068-2-6 (Vibration) 
E.	CE
F.	WEEE: Article 11 – Anex V Directive 2012 2012/19/EU

2.11	STANDARD ACCESSORIES
A.	Operations Manual

2.12	MANUFACTURED UNITS REFERENCE TABLES
Product	Description	IEEE/Ansi Standards	
Vi30120	8 + 2-port PoE Powered PoE Network Switch 	IEEE 802.3az
IEEE 802.3bz
IEEE 802.1p
IEEE 802.3q
IEEE 802.3af
IEEE 802.3at
IEEE 802.3bt	
Table A. Compatible ANSI/ IEEE Standards

Product	Compatible Ethernet Equipment	
Vi30210 	All products are compliant to standard IP Ethernet protocols.	
Table B. Compatible Ethernet Equipment 

Product	Accessories	Per Port Power Outputs*	Description	
Vi30210 	Vi1120	120W/54VDC Desktop PS 	Brick Power Supply	
	Vi10120	120W/54VDC PS 	DIN Rail, Harden, Redundant 	
	Vi10240	240W/54VDC PS 	DIN Rail, Harden, Redundant	
	Vi10480	480W/54VDC PS  	DIN Rail, Harden, Redundant	
Table C: Optional Accessories
* Port output power is determined by the number and power requirements of the connected devices. Based on the examples above, if only 2 devices are connected, the port output power is doubled.

Vigitron reserves the right to change products or specifications without notice.

END OF SECTION