DIVISION 27 21 29
Vi30005WP 5-port IP67 Weatherproof PoE Powered PoE Network Switch
PART 1 - GENERAL
1.1	SUMMARY
A.	5-port IP67 Weatherproof PoE Powered PoE Network Switch  

1.2	SECTION INCLUDES
A.	Vi30005WP 5-port IP67 Weatherproof PoE Powered PoE Network Switch

1.3	REFERENCES
A.	European Union Compliance (CE)
B.	Rohs
C.	WEEE Compliant 
D.	FCC
E.	CE

1.4	SYSTEM DESCRIPTION
A.	Performance Requirements: Provide 5 ports for network switching, one port can be used for powering via PoE and four ports can be used for providing PoE to external devices. 
B.	The system shall utilize TIA/EIA 568-B cable connected to an RJ-45 plug. 

1.5	SUBMITTALS
A.	Manufacturer’s Installation and Operating Manual: Printed Installation and Operating Information
B.	Warranty: Manufacturer’s Printed Warranty

1.6	DELIVERY, STORAGE AND HANDLING
A.	Store in original packaging in a climate controlled environment. 
B.	Storage temperature not to exceed: -40˚C to +85˚C

1.7	PROJECT/SITE CONDITIONS
A.	Temperature Requirements: Product shall operate in an environment with an ambient temperature range of -40˚C to +75˚C using internal component fans.
B.	Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 90% (non-condensing). 

1.8	WARRANTY
A.	Limited Lifetime Warranty: Vigitron guarantees product to be free of defects for product lifetime, defined as the time that product is in production plus 3 years from end of production.

PART 2 - PRODUCTS
2.01	MANUFACTURER
A.	Acceptable Manufacturer: 
1.	Vigitron, Inc.: 7810 Trade Street Suite 100, San Diego, CA 92121, USA 
2.	Phone: +1 (858) 484-5209
3.	Email: support@vigitron.com
B.	Substitutions: Not Permitted

2.02	MANUFACTURED UNITS
A.	Reference Table A: Compatible ANSI/IEEE Standards 
B.	Reference Table B: Compatible Ethernet Equipment

2.03	GENERAL SPECIFICATIONS
A.	The switch shall contain 5 active ports. 
B.	All ports shall automatically detect network speeds of 100Mbps and 1,000Mbps.
C.	All ports shall support network speeds up to 1'000Mbps.  
D.	The switch shall support internal bandwidth up to 1'000Mbps.
E.	The switch shall be Vigitron model Vi30005WP. 
F.	Standard Ethernet Ports:
1.	The device shall have 5 standard Ethernet ports and 1 SFP port in a compact housing. The Ethernet port shall comply with: 
a.	IEEE 802.3u 100BaseT 
b.	IEEE 802.3az 1000BaseT 
2.	The SFP port shall comply with MSA standards.
3.	The standard ports of device shall support standard Ethernet UTP connection distances up to 100m.
4.	The SFP port shall be set at 100/1000Mbps but able to accept SFP up to 1Gbps.
G.	Port bandwidth settings shall be done by automatically.
H.	Input power can be up to 72W UPoE compliant. 
I.	Port PoE allocations shall be done automatically depending on load power requirements.
J.	The switch shall provide an overall power supply, depending upon its power input either by PoE or extender power supply. If it’s powered by an external power source of: 
1.	Up to 36W will be available at each port.
2.	Input can be powered up to 74W UPoE compliant 
3.	If it’s powered by a local power supply, the power available at each port shall be divided by four.
a.	If the local power usage is 120W @ 57 volts.
1.	Each port shall be able to provide 36W PoE. 
K.	The Vi30005WP can be positioned up to 328 ft. (100m) from a PoE power source in compliance with Ethernet transmission standards. 
L.	The switch shall have built-in smart PoE power allocation providing the required PoE camera power up to 36W per port. 
M.	The switch shall have built-in over power protection, shutting down power if the PoE budget is exceeded. 

2.04	DATA SPECIFICATIONS
A.	Data Interface: Passage of Data Compliant to -
1.	RFC 768 UDP
2.	RFC 2068 HTTP
3.	RFC 793 TCP
4.	RFC 791 IP
5.	RFC 1783 TFTP
6.	RFC 894 IP over Ethernet
7.	RFC 2544 TCP/IP Packet Transmission
B.	Port Data Rate: 100/1000Mbps
C.	Data Connections: 
1.	5 Standard Ethernet Ports
D.	Port PoE Power Outputs: 
1.	15.4W compliant to IEEE 802.3af ports
2.	36W complaint to IEEE 802.3at Type 1 and Type 2  
E.	Power consumption shall be 4W for basic switch functions.
F.	The D.C. input connector shall be a terminal block.

2.05	SPECIFICATIONS AND FEATURE SETS
A.	The Vi30005WP transmits and receives Ethernet data. 
1.	Internal bandwidth shall be constant with no more than a 2% decrease, when the input signal varies from a size of 64 bytes to 10,000 bytes using bidirectional transmission. 
2.	Internal bandwidth shall be constant over the quoted extended distance with no more than 2% decrease when: 
a.	Bidirectional signals are transmitted with a packet size of 10,000 bytes.
b.	Unidirectional signals are transmitted with a packet size of 10,000 bytes.
c.	Bandwidth shall remain the same for both upload and download operation.
B.	Packet losses shall be at 2% or less at packet sizes, ranging from 64 bytes to 10,000 bytes bidirectional unidirectional at 1000Mbps.
C.	Packets per second (PPS) shall not vary more than 2% at packet sizes, ranging from 64 bytes to 10,000 bytes bidirectional transmission. 
D.	Maximum distance from switch port to device shall be 328 ft. (100m) for data and PoE.
E.	The switch shall be compliant with IEEE 802.3az as detailed in the Energy Efficient Ethernet Task. It has the ability to automatically turn off PoE when link down is detected and/or idle, and resume without packet loss when link up is detected. 
F.	Each port shall be continuously monitored for potential overcurrent conditions. 
G.	The device must have the ability for PoE functionality in compliance with IEEE 802.3af/at standards when communicating with a PD: 
1.	Provide detection pulses to PD.
2.	Provide Classification pulses to PD and report via GUI. 
3.	Ability to provide Class 0, 1, 2, 3, and 4 IEEE 802.3af/at PoE power to PD, depending on power supplied without the need for a local power supply. 
4.	Provide auto-sensing for connected devices and individual port power up to 36W (IEEE 802.3at). 
H.	The switch shall provide for locking specific MAC addresses to specific ports, while user programming shall limit the number of allowed 1K MAC addresses per port. 
I.	The switch shall allow firmware upgrades via HTTP/HTTPs and TFTP, in addition to directly via an on-board console port.
J.	The switch shall support IEEE 802.1Q.

2.06	CONNECTORS
A.	Power Inlet: Terminal Block 
B.	Standard Ethernet: RJ-45, IEC 60603-7

2.07	ELECTRICAL SPECIFICATIONS
A.	External Power Supply:
1.	12VDC @ 3 amps - No PoE Output
2.	65W or greater @ 48V for all ports provide IEEE 802.3af compliant PoE. 
3.	124W or greater @ 48V for all ports provide IEEE 802.3at compliant PoE.
B.	PoE Output Power (depends on external or PoE power supplied):
1.	15.4W IEEE 802.3af Compliant  
2.	36W IEEE 802.3at Compliant 

2.08	MECHANICAL SPECIFICATIONS (Engineering to supply) 
E.	Dimensions (H x W x L): 1.84 x 5.42 x 6.61 in.; 4.67 x 13.8 x 16.8 cm 
F.	Finish: ABS plastic, UL rating of 94V-0
G.	Weight: 2.06lbs (934g) 

2.09	ENVIRONMENTAL SPECIFICATIONS
A.	Operating Temperature: -30˚C to +75˚C
B.	Storage Temperature: -40˚C to +85˚C
C.	Relative Humidity: 0% to 95% (non-condensing)

2.10	REGULATORY AGENCIES/APPROVALS AND LISTINGS
A.	FCC Part 15, Subpart A
B.	Emission Standards: 
1.	FCC Part 15, Subpart B, Class A
2.	EN 55022:2006+A1:2007
3.	EN 61000-3-2:2006+A1:2009+A2:2009
4.	EN 61000-3-3:2008
5.	EN 55024:1998+A1:2001+A2:2003
C.  RoHS
D.	CE

2.11	STANDARD ACCESSORIES
A.	Operations Manual

2.12	MANUFACTURED UNITS REFERENCE TABLES
Product	Description	IEEE/Ansi Standards	
Vi30005WP	5-port PoE Powered PoE Network Switch 	IEEE 802.3af
IEEE 802.3at
IEEE 802.3az
IEEE 802.1p
IEEE 802.3q
72W input UPoE compliant 
74W UPoE compliant port power when used with Vi00016 	
Table A. Compatible ANSI/ IEEE Standards

Product	Compatible Ethernet Equipment	
Vi30005WP 	All products are compliant to standard IP Ethernet protocols.	
Table B. Compatible Ethernet Equipment 

Vigitron reserves the right to change products or specifications without notice.

END OF SECTION